Training Aid to Assist in Developing Smoke Containment Systems – Zoned Smoke Control System Testing

- Normal HVAC Mode - Baseline

  - HVAC system is in normal operation without any call for an event.

  - Identify and verify all smoke barrier doors that separate the floor smoke zones are closed.

Measure and record the pressure differential across all smoke control zones that divide a building floor

- Smoke Control Mode for Each Smoke Control Zone – Event

  - Each separate control zone shall be activated and tested.

    - Testing shall not generate a false call to the fire department

  - Verify each Smoke Control Zone is activated.

  - Verify operational status of HVAC unit matched sequence of operations.

  - Verify the operation of all applicable fans, dampers, doors, and related equipment.

    - Fans: Confirm 1.5 times the number of require belts with a minimum of 2 (IFC 909.10.5)

    - Fans: Confirm Actual Current Draw and a minimum Service Factor of 1.15. (IFC 909.10.5)

  - Identify and verify all smoke barrier doors that separate the floor smoke zones are closed

  - Measure and record the pressure differential across all smoke barriers or doors that separate smoke zone from an adjacent zone.

    - Confirm pressure differential is at or above the minimum pressure differential.

    - Clearly indicate high and low pressure side of smoke barrier or door.

    - If a door opens due to air pressure, take one measurement with door closed and one with door opened by the pressure.

  - Repeat test until all alarm inputs have been activated.

  - Report the actual test conditions and results to the AHJ and engineer of record.

    - Deficiencies will require a clear plan of action and temporary accommodations.

  - Ensure that the SCS systems are deactivated and the associated HVAC systems are returned to their normal operation.

This document is intended to be used solely as an aide when developing the methods, procedures, and forms used in the inspection of Smoke Control Systems (SCS).  It is the responsibility of each contractor, supervisor, and technician to ensure that the methods, procedures, and forms used meet the requirements of the local mechanical and fire codes. Furthermore, it is the responsibility of the SCS Supervisor or contractor to submit the methods, procedures, and forms that it drafts directly to the Authority Having Jurisdiction (AHJ) for approval, prior to performing the actual work.  The National Energy Management Institute Committee makes no representations, whatsoever, that drafting procedures or forms based on this document will meet that requirement of local mechanical and fire codes and expressly disclaims any liability or responsibility regarding the use of this document.