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Training Aid to Assist in Developing Smoke Management Systems in Large Volume Spaces Testing 

1) Determine the perimeter of the Large Volume Space.
2) Identify all doors and openings, that will remain open during an event.
3) Activate the Smoke Management System
i. Ensure that the system is in test and a signal will not be sent to the fire department.
4) Verify the operation of all applicable fans, dampers, doors, and related equipment.
i. Fans: Confirm 1.5 times the number of required belts with a minimum of 2 (IFC 909.10.5)
ii. Fans: Confirm Actual Current Draw and a minimum Service Factor of 1.15. (IFC 909.10.5)
5) Measure Exhaust Fan volume and record operating data.
6) Traverse the velocity of makeup air at large openings.
7) If applicable, measure supply grilles served by a makeup air system
8) Measure the door force required to open all exit doors.
i. Confirm door force is below maximum allowed.  

This document is intended to be used solely as an aide when developing the methods, procedures, and forms used in the inspection of Smoke Control Systems (SCS).  It is the responsibility of each contractor, supervisor, and technician to ensure that the methods, procedures, and forms used meet the requirements of the local mechanical and fire codes. Furthermore, it is the responsibility of the SCS Supervisor or contractor to submit the methods, procedures, and forms that it drafts directly to the Authority Having Jurisdiction (AHJ) for approval, prior to performing the actual work.  The National Energy Management Institute Committee makes no representations, whatsoever, that drafting procedures or forms based on this document will meet that requirement of local mechanical and fire codes and expressly disclaims any liability or responsibility regarding the use of this document. 


